## Verdber1 VDI 2089 B1-94
according to VDI 2089 Bl.1 / 94
Project pool hall
technical data of the pool hall:
pool 1
volumen room | R ca. | 2000 | m3
pool surface | A | 261 | m2
pool temperature | tW | 32 | °C | 47.53
steam pressure: water 100% rel.F. | Ps | 47.53 | mbar | 22.8126
room temp. | tR | 32 | °C
room humi. | rel.F. | 48 | % |  |  |  |  | g/kg (Soll X acc. VDI 14,3 g/kg)
steam pressure: air | Pd | 22.81 | mbar = X Ist 14.33 g/kg (Soll X acc. VDI 14,3 g/kg) |  |  |  |  | mbar = X Ist
empiric scale bathing operation: | Nf | 22 | [5 empty] | 14.33
empiric scale rest operation: | Nf | 5
calculation of evaporation |  |  |  |  | pool usage | 14 | hr/d | kg/h W=
max. quantity of evaporation: | W max = | 141.98 | kg/h W= 0.544 kg/m2h W max/d = |  |  | 1987.7 | kg/d | 0.544 | kg/m2h W max/d =
min. quantity of evaporation: | W min = | 32.27 | kg/h W= 0.124 kg/m2h W min/d = |  |  | 322.7 | kg/d | 0.124 | kg/m2h W min/d =
max. airvolumenflow: | max. VL = | 23163 | m3/h | W mid./d = |  | 96.3 | kg/h
pool 2
volumen room | R ca. | 0 | m3
pool surface | A | 12 | m2
pool temperature | tW | 15 | °C | 17.05
steam pressure: water 100% rel.F. | Ps | 17.05 | mbar | 22.8126
room temp. | tR | 32 | °C
room humi. | rel.F. | 48 | % |  |  |  |  | g/kg (Soll X acc. VDI 14,3 g/kg)
steam pressure: air | Pd | 22.81 | mbar = X Ist 14.33 g/kg (Soll X acc. VDI 14,3 g/kg) |  |  |  |  | mbar = X Ist
empiric scale bathing operation: | Nf | 20 | [5 empty] | 14.33
empiric scale rest operation: | Nf | 5
calculation of evaporation |  |  |  |  | pool usage | 14 | hr/d | kg/h W=
max. quantity of evaporation: | W max = | -1.38 | kg/h W= -0.115 kg/m2h W max/d = |  |  | -19.3 | kg/d | -0.115 | kg/m2h W max/d =
min. quantity of evaporation: | W min = | -0.35 | kg/h W= -0.029 kg/m2h W min/d = |  |  | -3.5 | kg/d | -0.029 | kg/m2h W min/d =
max. airvolumenflow: | max. VL = | -225 | m3/h | W mid./d = |  | -1 | kg/h
pool 3
volumen room | R ca. | 0 | m3
pool surface | A | 60 | m2
pool temperature | tW | 32 | °C | 47.53
steam pressure: water 100% rel.F. | Ps | 47.53 | mbar | 22.8126
room temp. | tR | 32 | °C
room humi. | rel.F. | 48 | % |  |  |  |  | g/kg (Soll X acc. VDI 14,3 g/kg)
steam pressure: air | Pd | 22.81 | mbar = X Ist 14.33 g/kg (Soll X acc. VDI 14,3 g/kg) |  |  |  |  | mbar = X Ist
empiric scale bathing operation: | Nf | 30 | [5 empty] | 14.33
empiric scale rest operation: | Nf | 5
calculation of evaporation |  |  |  |  | pool usage | 14 | hr/d | kg/h W=
max. quantity of evaporation: | W max = | 44.52 | kg/h W= 0.742 kg/m2h W max/d = |  |  | 623.3 | kg/d | 0.742 | kg/m2h W max/d =
min. quantity of evaporation: | W min = | 7.42 | kg/h W= 0.124 kg/m2h W min/d = |  |  | 74.2 | kg/d | 0.124 | kg/m2h W min/d =
max. airvolumenflow: | max. VL = | 7263 | m3/h | W mid./d = |  | 29.1 | kg/h
W max ges. = 185.12 kg/h W min ges. = 39.34 kg/h W mid.C59/d ges. = 124.4 kg/h
Complete air volumen flow:
max. air volumen flow: | max. VL = | 30201 | m3/h according to data, mixed air units
used unit type: | FAM25000 | 28000 | m3/h according to data, mixed air units
| air changing rate = | 14 | times/hr | VL mid. = | 20295 | m3/h
Red areas are filled by yourself !
e empiric scale of total evaporation [g/(hPa m2 h)]:
0,5 = rest operation (covered)
5,0 = rest operation (not covered).
15 = private pool
20 =public pool (mid size)
28 = public pools (big size with attractions)
35 = whirlPool
GEA Happel - Fricostar